## setup
Set Project and Month |  | month | month_str | month_num | days in month | project | sub_project1 | sub_project2
current year | 2021 | January | 01 | 1 | 31 | Milford 1 | Milford 1 Clipper | Milford 1 GE
current month | December | February | 02 | 2 | 28 | Milford 2 | Milford 2 GE
project | Weaver | March | 03 | 3 | 31 | El Campo
project capacity (MW) | 72.6 | April | 04 | 4 | 30 | Weaver
number of turbines | 22 | May | 05 | 5 | 31 | Howard
|  | June | 06 | 6 | 30 | Highland North
Date Calculations |  | July | 07 | 7 | 31 | Mustang Hills
month_num | 12 | August | 08 | 8 | 31 | Patton
month_str | 12 | September | 09 | 9 | 30 | Twin Ridges
days_in_current_month | 31 | October | 10 | 10 | 31
days_in_current_year | 365 | November | 11 | 11 | 30
|  | December | 12 | 12 | 31
Connection Authorizations
dropbox token | C8HO860vI7gAAAAAAAAAAVz69G_NHVL16gQvkW5KeP9-nzyvgZIaxC-SdeiLlTEa
Passwords
password to edit | lre
Data Path
csv data path | /LR Team/LR Corporate/Asset Management/Engineering/Monthly reports/Wind/2021/202112/Weaver/data
File Names
YTD perf | ytd_perf_Weaver.csv
Turbine perf | turbine_perf_Weaver.csv
Daily perf | daily_perf_Weaver.csv
All turbine category losses | losses_by_turbine_mwh_Weaver.csv
Total category losses | offline_category_loss_mwh_Weaver.csv
Fault summary | fault_summary_Weaver.csv
Calculated sources:
ytd_path | /LR Team/LR Corporate/Asset Management/Engineering/Monthly reports/Wind/2021/202112/Weaver/data/ytd_perf_Weaver.csv
turbine_path | /LR Team/LR Corporate/Asset Management/Engineering/Monthly reports/Wind/2021/202112/Weaver/data/turbine_perf_Weaver.csv
daily_path | /LR Team/LR Corporate/Asset Management/Engineering/Monthly reports/Wind/2021/202112/Weaver/data/daily_perf_Weaver.csv
all_loss_path | /LR Team/LR Corporate/Asset Management/Engineering/Monthly reports/Wind/2021/202112/Weaver/data/losses_by_turbine_mwh_Weaver.csv
total_loss_path | /LR Team/LR Corporate/Asset Management/Engineering/Monthly reports/Wind/2021/202112/Weaver/data/offline_category_loss_mwh_Weaver.csv
faults_path | /LR Team/LR Corporate/Asset Management/Engineering/Monthly reports/Wind/2021/202112/Weaver/data/fault_summary_Weaver.csv
Formulas:
days in month = EOMONTH(DATE(curr_year,[month_num],1),0)-DATE(curr_year,[month_num],1)+1

## variables
Variables to populate word doc
| ##S | project_txt | Weaver
| ##S | sub_project_1_txt
| ##S | sub_project_2_txt
| ##S | Year | 2021
| ##S | Month | December
|  | month date | 2021-12-01
days in month
|  | hrs in month | 744
| ##S | month_energy | 24224.578
| ##S | month_budget_energy | 22899.871
| ##S | month_energy_diff | 1324.707 | ##S | month_energy_diff_sign | above
| ##S | month_percent_e_diff | 5.785%
| ##S | month_wind | 7.923
| ##S | month_cf | 44.85%
| ##S | month_prcnt_budget | 100.1%
| ##S | month_availability | 98.46%
| ##S | month_contract_avail | 98.89%
| ##S | month_pi
| ##S | ytd_energy | 219291.17
| ##S | ytd_budget_energy | 218658.718
| ##S | ytd_energy_diff | 632.452 | ##S | ytd_energy_diff_sign | above
| ##S | ytd_percent_e_diff | 0.2892%
| ##S | ytd_availability | 92.19%
| ##S | ytd_contract_avail | 98.56%
| ##S | ytd_pi
| ##S | budget_availability | 96.5% | ##S | budget_avail_type | contract
| ##S | budget_project_avail | 90.2%
| ##S | budget_contract_avail | 96.5%
Note on D31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Change to 90.2% starting 2021-11

## Table curtailment
241 | 69 | 80 | 233 | 1
The project had no balance of plant or offtaker directed curtailment for the month.
Table 7.1 Balance of Plant and Offtaker Curtailment
+ | + | + | -
Description | Start Date | End Date | Reason
No grid curtailments this month

## Table site summary
|  |  | 110 |  | 69 |  | 64 |  | 56 |  | 63 |  | 77 | [7 empty] | 71 |  |  |  | 55 |  | 75 |  |  |  |  | -16
##S | Table_5.1
##RS
Query site performance from data lake
| capacity_MW | 72.6 | [31 empty] | current month:
|  |  | Table 5.1 Site Summary | [30 empty] | 25039.472 | 391.7528 | 280.8573 | 154.6238
|  |  | + | + | + | + | + | + | + | + | + | + | + | + | + | + | + | - | - | - | - | - | - | + | + | + | + | - |  | Calc data |  | Plot data |  | Avail loss data
| month number | days in month | Month |  | Net Energy (MWh) |  | Budget Energy (MWh) |  | Variance (%) |  | Net Capacity Factor (%) |  | Project Availability (%) |  | Turbine Availability (%) |  | Contract Availability (%) |  | O&M Reported Contract Avail (%) |  | Budget Availability (%) |  | Performance Index (%) |  | Wind Speed (m/s) |  | Budget Wind Speed (m/s) | % of Resource | + | wind * days in month | budget wind * days in month | YTD energy | YTD budget | Turbine export energy (MWh) | Project lost energy (MWh) | Contract lost energy (MWh) | Turbine lost energy (MWh)
| 1 | 31 | January |  | 22185.555 |  | 23466.517 |  | -5.459% |  | 41.07% |  | 94.46% |  | 94.98% |  | 95.43% |  | - |  | 96.5% |  | 99.07% |  | 7.3456 |  | 8.1 | 74.58% | + | 227.7144 | 251.1 | 22185.555 | 23466.517 | 22918.8312 | 1345.1954 | 1096.7789 | 1212.2536
| 2 | 28 | February |  | 16838.995 |  | 21112.238 |  | -20.24% |  | 34.52% |  | 94.56% |  | 95.13% |  | 95.24% |  | - |  | 96.5% |  | 91.8% |  | 7.2773 |  | 8.14 | 71.46% | + | 203.7645 | 227.92 | 39024.55 | 44578.755 | 17495.8528 | 1005.7484 | 873.9393 | 895.094
| 3 | 31 | March |  | 29746.721 |  | 23626.863 |  | 25.9% |  | 55.07% |  | 98.6% |  | 99.52% |  | 99.54% |  | - |  | 96.5% |  | 99.52% |  | 8.9502 |  | 8.3 | 125.4% | + | 277.4547 | 257.3 | 68771.271 | 68205.618 | 30630.208 | 434.7305 | 142.4441 | 148.2238
| 4 | 30 | April |  | 20841.72 |  | 19939.899 |  | 4.523% |  | 39.87% |  | 96.87% |  | 98.41% |  | 99% |  | - |  | 96.5% |  | 94.05% |  | 7.5803 |  | 7.48 | 104.1% | + | 227.4103 | 224.4 | 89612.991 | 88145.517 | 21498.698 | 693.552 | 217.184 | 346.5155
| 5 | 31 | May |  | 17271.181 |  | 15744.38 |  | 9.697% |  | 31.98% |  | 86.8% |  | 95.38% |  | 98.86% |  | - |  | 96.5% |  | 101.7% |  | 6.6129 |  | 6.65 | 98.33% | + | 204.9991 | 206.15 | 106884.172 | 103889.897 | 17873.665 | 2718.2017 | 206.8338 | 866.4994
| 6 | 30 | June |  | 17003.132 |  | 13169.845 |  | 29.11% |  | 32.53% |  | 91.36% |  | 99.21% |  | 99.2% |  | - |  | 96.5% |  | 99.95% |  | 6.6986 |  | 6.26 | 122.5% | + | 200.9585 | 187.8 | 123887.304 | 117059.742 | 17541.457 | 1658.6782 | 142.1313 | 140.4086
| 7 | 31 | July |  | 10830.961 |  | 11649.166 |  | -7.024% |  | 20.05% |  | 85.27% |  | 99.72% |  | 99.75% |  | - |  | 96.5% |  | 99.18% |  | 5.6822 |  | 5.89 | 89.79% | + | 176.1486 | 182.59 | 134718.265 | 128708.908 | 11310.103 | 1953.1278 | 28.1614 | 31.6619
| 8 | 31 | August |  | 7319.614 |  | 10887.875 |  | -32.77% |  | 13.55% |  | 73.8% |  | 99.65% |  | 99.67% |  | - |  | 96.5% |  | 101.1% |  | 5.0678 |  | 5.88 | 64.02% | + | 157.1023 | 182.28 | 142037.879 | 139596.783 | 7758.472 | 2754.0738 | 25.5963 | 27.4125
| 9 | 30 | September |  | 16027.069 |  | 14415.958 |  | 11.18% |  | 30.66% |  | 89.56% |  | 99.44% |  | 99.41% |  | - |  | 96.5% |  | 100.4% |  | 6.5263 |  | 6.58 | 97.57% | + | 195.7885 | 197.4 | 158064.948 | 154012.741 | 16609.632 | 1935.7779 | 98.6644 | 93.2592
| 10 | 31 | October |  | 16032.604 |  | 20804.727 |  | -22.94% |  | 29.68% |  | 97.88% |  | 98.99% |  | 98.26% |  | - |  | 96.5% |  | 99.17% |  | 6.6201 |  | 7.47 | 69.6% | + | 205.2225 | 231.57 | 174097.552 | 174817.468 | 16596.274 | 358.7197 | 293.26 | 169.4043
| 11 | 30 | November |  | 20969.04 |  | 20941.379 |  | 0.1321% |  | 40.12% |  | 98.7% |  | 99.47% |  | 99.47% |  | - |  | 96.5% |  | 99.9% |  | 7.2239 |  | 7.64 | 84.53% | + | 216.7158 | 229.2 | 195066.592 | 195758.847 | 21863.933 | 288.7243 | 116.6067 | 117.532
| 12 | 31 | December |  | 24224.578 |  | 22899.871 |  | 5.785% |  | 44.85% |  | 98.46% |  | 99.39% |  | 98.89% |  | - |  | 96.5% |  | 97.99% |  | 7.923 |  | 7.83 | 103.6% | + | 245.6138 | 242.73 | 219291.17 | 218658.718 | 25039.472 | 391.7528 | 280.8573 | 154.6238
| days ytd: | 365 | Year to Date |  | 219291.17 |  | 218658.718 |  | 0.2892% |  | 34.48% |  | 92.19% |  | 98.27% |  | 98.56% |  | #DIV/0! |  | 96.5% |  | 98.65% |  | 6.959 |  | 7.185 | 90.86% | +
|  | 0 | [22 empty] | weighted avg: |  |  |  | ##RE
[25 empty] | 6.9559 |  | 7.1793
90.86%
90.95%
90.97%
formatting
[32 empty] | row height | 15

## Table site summary_1
|  | 82 | 5 | 64 | 2 | 64 | 2 | 64 | 2 | 64 | 2 | 64 | 2 | 64 | 2 | 64 | 2 | 75 |  | 0
##S | Table_5.1a
##RS
Table 5.1a Site Summary Blank
|  | Month |  | Net Energy (MWh) |  | Budget Energy (MWh) |  | Variance (%) |  | Capacity Factor (%) |  | Project Availability (%) |  | Budget Availability (%) |  | Wind Speed (m/s) |  | Budget Wind Speed (m/s)
|  | January |  | 19889 |  | 21276 |  | -6.5 |  | 18.4 |  | 92 |  | 93.2 |  | 5.3 |  | 5.2
|  | February |  | 21982 |  | 19644 |  | 11.9 |  | 22.6 |  | 92.1 |  | 92.2 |  | 5.7 |  | 5.6
|  | March |  | 30933 |  | 25198 |  | 22.8 |  | 28.7 |  | 91.9 |  | 93.2 |  | 7.1 |  | 6.4
|  | April |  | 20857 |  | 28405 |  | -26.6 |  | 20 |  | 89.5 |  | 92.5 |  | 5.8 |  | 7
|  | May |  | 28753 |  | 28060 |  | 2.5 |  | 26.7 |  | 89.1 |  | 92.7 |  | 7.3 |  | 6.8
|  | June |  | 25388 |  | 28822 |  | -11.9 |  | 24.3 |  | 85.2 |  | 93.2 |  | 7 |  | 7.2
|  | July |  | 27622 |  | 28159 |  | -1.9 |  | 25.7 |  | 86 |  | 92.9 |  | 7 |  | 6.8
|  | August |  | - |  | 29567 |  | - |  | - |  | - |  | 93.1 |  | - |  | 7.1
|  | September |  | - |  | 24246 |  | - |  | - |  | - |  | 93.4 |  | - |  | 6
|  | October |  | - |  | 22697 |  | - |  | - |  | - |  | 91.7 |  | - |  | 5.7
|  | November |  | - |  | 20313 |  | - |  | - |  | - |  | 93.4 |  | - |  | 5.5
|  | December |  | - |  | 20639 |  | - |  | - |  | - |  | 92.9 |  | - |  | 5.4
|  | Year to Date |  | 175424 |  | 179564 |  | -2.3 |  | 23.7714 |  | 89.4 |  | 92.8667 |  | 6.4 |  | 6.225
| 0 | [17 empty] | ##RE

## Table site summary_2
|  | 82 | 5 | 64 | 2 | 64 | 2 | 64 | 2 | 64 | 2 | 64 | 2 | 64 | 2 | 64 | 2 | 75 |  | 0 | 0
##S | Table_5.1b
##RS
Table 5.1b Site Summary Blank
|  | Month |  | Net Energy (MWh) |  | Budget Energy (MWh) |  | Variance (%) |  | Capacity Factor (%) |  | Project Availability (%) |  | Budget Availability (%) |  | Wind Speed (m/s) |  | Budget Wind Speed (m/s)
|  | January |  | 8833 |  | 9547 |  | -7.5 |  | 20.3 |  | 97.8 |  | 98.7 |  | 4.7 |  | 4.1
|  | February |  | 10138 |  | 9010 |  | 12.5 |  | 25.8 |  | 99.4 |  | 98.7 |  | 5.2 |  | 4.5
|  | March |  | 14712 |  | 11641 |  | 26.4 |  | 33.8 |  | 99.2 |  | 98.6 |  | 6.4 |  | 5.2
|  | April |  | 10404 |  | 13378 |  | -22.2 |  | 24.7 |  | 98.1 |  | 97.9 |  | 4.9 |  | 5.8
|  | May |  | 14344 |  | 13239 |  | 8.3 |  | 33 |  | 98 |  | 98.8 |  | 6.6 |  | 5.6
|  | June |  | 13027 |  | 13606 |  | -4.3 |  | 30.9 |  | 96.9 |  | 98.8 |  | 6.3 |  | 6
|  | July |  | 14941 |  | 13218 |  | 13 |  | 34.3 |  | 97.5 |  | 98.5 |  | 6.6 |  | 5.6
|  | August |  | - |  | 13950 |  | - |  | - |  | - |  | 98.7 |  | - |  | 6.1
|  | September |  | - |  | 11189 |  | - |  | - |  | - |  | 98.8 |  | - |  | 4.9
|  | October |  | - |  | 10392 |  | - |  | - |  | - |  | 97.3 |  | - |  | 4.6
|  | November |  | - |  | 9127 |  | - |  | - |  | - |  | 98.7 |  | - |  | 4.4
|  | December |  | - |  | 9279 |  | - |  | - |  | - |  | 98.4 |  | - |  | 4.2
|  | Year to Date |  | 86399 |  | 83639 |  | 3.3 |  | 28.9714 |  | 98.1286 |  | 98.5 |  | 5.8143 |  | 5.1
| 0 | [17 empty] | ##RE

## Table wtg perf_1
##S | Table_6.1a |  | 98 | 3 | 74 | 3 | 65 | 3 |  |  | 74 | 3 |  |  | 77 | 3 | 74 | 3 |  |  | 71 | 3 | 71
##S | Table_6.1aheader
##S | Table_6.1atitle
Performance table updated from data lake
6.1 Performance Tables
| capacity_MW | 72.6 | Table 6.1(a) Turbine Performance
|  |  | + | + | + | + | + | + | + | + | + | + | + | + | + | - | - | - | - | - | - | + | -
|  |  | Turbine |  | Energy Export (MWh) |  | Capacity Factor |  | Wind Speed (m/s) |  | Contract Availability |  | Turbine Availability |  | Project Availability |  | Contract Lost Energy (MWh) |  | Turbine Lost Energy (MWh) |  | Project Lost Energy (MWh) |  | Performance Index | +
|  |  | Weaver 3 |  | 1040.019 |  | 42.36% |  | 7.4516 |  | 98.54% |  | 99.73% |  | 98.34% |  | 15.4206 |  | 2.7985 |  | 17.5807 |  | 98.29% | +
|  |  | Weaver 4 |  | 1086.746 |  | 44.26% |  | 7.8317 |  | 99.88% |  | 99.88% |  | 99.76% |  | 1.2664 |  | 1.3228 |  | 2.5891 |  | 99.07% | +
|  |  | Weaver 5 |  | 1055.195 |  | 42.98% |  | 7.542 |  | 97.47% |  | 99.88% |  | 97.36% |  | 27.3974 |  | 1.2663 |  | 28.6613 |  | 98.29% | +
|  |  | Weaver 6 |  | 1073.404 |  | 43.72% |  | 7.9623 |  | 99.82% |  | 99.84% |  | 99.67% |  | 1.9486 |  | 1.712 |  | 3.5767 |  | 95.22% | +
|  |  | Weaver 7 |  | 1088.642 |  | 44.34% |  | 7.7842 |  | 98.19% |  | 99.79% |  | 98.09% |  | 20.1154 |  | 2.248 |  | 21.201 |  | 97.33% | +
|  |  | Weaver 8 |  | 1181.301 |  | 48.11% |  | 8.2494 |  | 97.5% |  | 99.84% |  | 97.45% |  | 30.2694 |  | 1.8343 |  | 30.8737 |  | 97.94% | +
|  |  | Weaver 9 |  | 1124.325 |  | 45.79% |  | 7.9495 |  | 97.08% |  | 99.9% |  | 96.98% |  | 33.8591 |  | 1.1134 |  | 34.9622 |  | 97.85% | +
|  |  | Weaver 10 |  | 1065.674 |  | 43.4% |  | 7.823 |  | 97.41% |  | 97.45% |  | 96.95% |  | 28.3307 |  | 27.9087 |  | 33.5551 |  | 96.96% | +
|  |  | Weaver 11 |  | 1140.884 |  | 46.47% |  | 7.8488 |  | 99.71% |  | 99.81% |  | 99.54% |  | 3.2722 |  | 2.1654 |  | 5.2632 |  | 97.16% | +
|  |  | Weaver 12 |  | 1156.208 |  | 47.09% |  | 7.8026 |  | 99.66% |  | 99.88% |  | 99.57% |  | 3.9453 |  | 1.381 |  | 4.948 |  | 97.57% | +
|  |  | Weaver 13 |  | 1024.787 |  | 41.74% |  | 7.4801 |  | 99.9% |  | 99.85% |  | 99.76% |  | 1.0463 |  | 1.5883 |  | 2.4142 |  | 97.86% | +
|  |  | Weaver 14 |  | 1089.485 |  | 44.37% |  | 7.423 |  | 98% |  | 99.7% |  | 97.71% |  | 22.2231 |  | 3.3128 |  | 25.5359 |  | 103.1% | +
|  |  | Weaver 15 |  | 1113.237 |  | 45.34% |  | 7.8016 |  | 99.22% |  | 99.88% |  | 99.1% |  | 8.7348 |  | 1.3618 |  | 10.0967 |  | 97.49% | +
|  |  | Weaver 16 |  | 1120.916 |  | 45.65% |  | 7.7787 |  | 98.64% |  | 99.19% |  | 97.94% |  | 15.4118 |  | 9.1791 |  | 23.5939 |  | 98.45% | +
|  |  | Weaver 17 |  | 1334.034 |  | 54.34% |  | 8.7968 |  | 98.13% |  | 98.87% |  | 98.07% |  | 25.4639 |  | 15.264 |  | 26.2 |  | 98% | +
|  |  | Weaver 18 |  | 1348.888 |  | 54.94% |  | 8.9327 |  | 98.53% |  | 99.97% |  | 98.5% |  | 20.1138 |  | 0.40209 |  | 20.5159 |  | 97.24% | +
|  |  | Weaver 19 |  | 1243.662 |  | 50.65% |  | 8.3343 |  | 98.87% |  | 99.92% |  | 98.83% |  | 14.2353 |  | 1.0357 |  | 14.7489 |  | 97.12% | +
|  |  | Weaver 20 |  | 1108.965 |  | 45.17% |  | 7.6635 |  | 99.86% |  | 99.58% |  | 99.51% |  | 1.5832 |  | 4.6464 |  | 5.4736 |  | 97.4% | +
|  |  | Weaver 22 |  | 1049.749 |  | 42.76% |  | 7.4268 |  | 99.92% |  | 93.68% |  | 93.62% |  | 0.823 |  | 70.7663 |  | 71.5893 |  | 111.4% | +
|  |  | Weaver 23 |  | 1115.34 |  | 45.43% |  | 7.7563 |  | 99.92% |  | 99.92% |  | 99.85% |  | 0.8455 |  | 0.83934 |  | 1.6848 |  | 97.18% | +
|  |  | Weaver 24 |  | 1178.872 |  | 48.02% |  | 8.1501 |  | 99.69% |  | 99.9% |  | 99.61% |  | 3.7145 |  | 1.2198 |  | 4.6033 |  | 95.52% | +
|  |  | Weaver 25 |  | 1299.139 |  | 52.91% |  | 8.5175 |  | 99.94% |  | 99.9% |  | 99.84% |  | 0.83711 |  | 1.2577 |  | 2.0853 |  | 97.08% | +
|  |  | Turbine Averages |  | 1138.1578 |  | 46.36% |  | 7.923 |  | 98.9% |  | 99.38% |  | 98.46% |  | 12.7662 |  | 7.0284 |  | 17.8069 |  | 98.34% | -
|  |  | Site Totals |  | 25039.472 |  | 46.36% |  | 7.923 |  | 98.89% |  | 99.39% |  | 98.46% |  | 280.8573 |  | 154.6238 |  | 391.7528 |  | 98.34% | +
0

## Table wtg_perf_2
|  | 98 | 3 | 74 | 3 | 65 | 3 | 74 | 3 | 77 | 3 | 70 | 3 | 74 | 3 | 71 | 0
##S | Table_6.1b
##S | table_6.1bheader | + | + | + | + | + | + | + | + | + | + | + | + | + | + | +
Performance table updated from data lake
Table 6.1(b) Turbine Performance Blank
|  | Turbine |  | Energy Export (MWh) |  | Capacity Factor |  | Availability |  | Performance Index |  | Wind Speed (m/s) |  | Lost Energy Curtailment (MWh) |  | Lost Energy Offline (MWh)
|  | MIL01-0 6-13 |  | 396 |  | 35.4% |  | 99.7% |  | 101.1% |  | 5.7 |  | 0 |  | 1.2
|  | MIL01-05-10 |  | 409 |  | 36.6% |  | 99.9% |  | 94.7% |  | 6.9 |  | 0 |  | 0.5
|  | MIL01-05-11 |  | 411 |  | 36.8% |  | 99.9% |  | 90.1% |  | 7.1 |  | 0 |  | 0.4
|  | MIL01-05-12 |  | 343 |  | 30.7% |  | 88.8% |  | 94.6% |  | 6.8 |  | 0 |  | 43.2
|  | MIL01-05-13 |  | 417 |  | 37.3% |  | 100% |  | 93.4% |  | 7 |  | 0 |  | 0
|  | MIL01-05-14 |  | 420 |  | 37.6% |  | 98.6% |  | 93.5% |  | 7 |  | 0 |  | 6.1
|  | MIL01-05-15 |  | 430 |  | 38.5% |  | 99.2% |  | 93.4% |  | 7 |  | 0 |  | 3.4
|  | MIL01-05-16 |  | 346 |  | 27.6% |  | 84.4% |  | 94.3% |  | 6.2 |  | 0 |  | 63.9
|  | MIL01-05-17 |  | 456 |  | 40.8% |  | 100% |  | 93.7% |  | 7.1 |  | 0 |  | 0
|  | MIL01-05-18 |  | 420 |  | 37.7% |  | 93.8% |  | 86.3% |  | 7.2 |  | 0 |  | 27.8
|  | MIL01-06-01 |  | 393 |  | 35.2% |  | 100% |  | 91.8% |  | 6.7 |  | 0 |  | 0
|  | MIL01-06-02 |  | 383 |  | 34.3% |  | 100% |  | 93.6% |  | 6.5 |  | 0 |  | 0.2
|  | MIL01-06-03 |  | 392 |  | 35.1% |  | 99.9% |  | 93.6% |  | 6.7 |  | 0 |  | 0.6
|  | MIL01-06-04 |  | 370 |  | 33.2% |  | 97.8% |  | 91.3% |  | 6.7 |  | 0 |  | 8.5
|  | MIL01-06-05 |  | 388 |  | 34.7% |  | 99.9% |  | 93.3% |  | 6.6 |  | 0 |  | 0.3
|  | MIL01-06-06 |  | 395 |  | 35.4% |  | 99.1% |  | 93.9% |  | 6.6 |  | 0 |  | 3.5
|  | MIL01-06-07 |  | 408 |  | 36.6% |  | 99.6% |  | 83% |  | 5.8 |  | 0 |  | 1.8
|  | MIL01-06-08 |  | 398 |  | 35.6% |  | 95% |  | 91.2% |  | 6.5 |  | 0 |  | 20.8
|  | MIL01-06-09 |  | 426 |  | 38.2% |  | 100% |  | - |  | 7.1 |  | 0 |  | 0
|  | MIL01-06-10 |  | 395 |  | 35.3% |  | 100% |  | 94.4% |  | 6.7 |  | 0 |  | 0.2
|  | MIL01-06-11 |  | 379 |  | 33.9% |  | 100% |  | 94.9% |  | 6.7 |  | 0 |  | 0.1
|  | MIL01-06-12 |  | 386 |  | 34.6% |  | 100% |  | 93.1% |  | 6.1 |  | 0 |  | 0.2
|  | MIL01-06-14 |  | 367 |  | 32.9% |  | 97.7% |  | 93% |  | 6.6 |  | 0 |  | 8.7
|  | MIL01-06-15 |  | 375 |  | 33.6% |  | 98.3% |  | 88.6% |  | 6.8 |  | 0 |  | 6.5
|  | MIL01-06-16 |  | 396 |  | 35.5% |  | 99.8% |  | 93.9% |  | 6.7 |  | 0 |  | 0.7
|  | MIL01-07-01 |  | 450 |  | 40.3% |  | 99.8% |  | 94.3% |  | 7.2 |  | 0 |  | 1
|  | MIL01-07-02 |  | 437 |  | 39.2% |  | 99.7% |  | 94.1% |  | 6.8 |  | 0 |  | 1.4
|  | MIL01-07-03 |  | 391 |  | 35% |  | 96.7% |  | 94% |  | 6.4 |  | 0 |  | 13.5
|  | MIL01-07-04 |  | 378 |  | 33.8% |  | 98.6% |  | 94.1% |  | 6.6 |  | 0 |  | 5.5
|  | MIL01-07-05 |  | 286 |  | 25.7% |  | 82.5% |  | 93.1% |  | 6.5 |  | 0 |  | 60.6
|  | MIL01-07-06 |  | 360 |  | 32.2% |  | 97.7% |  | 93% |  | 6 |  | 0 |  | 8.5
|  | MIL01-07-07 |  | 376 |  | 33.7% |  | 99.8% |  | 92% |  | 6.7 |  | 0 |  | 0.9
|  | MIL01-07-08 |  | 388 |  | 35.3% |  | 99.6% |  | 93.2% |  | 6.7 |  | 0 |  | 1.7
|  | MIL01-07-09 |  | 396 |  | 35.4% |  | 99.1% |  | 95.1% |  | 6.5 |  | 0 |  | 3.5
|  | MIL01-07-10 |  | 392 |  | 35.1% |  | 98.6% |  | 92.6% |  | 6.2 |  | 0 |  | 5.5
|  | MIL01-07-11 |  | 299 |  | 26.7% |  | 77.7% |  | 92.5% |  | 6.7 |  | 0 |  | 85.5
|  | MIL01-07-12 |  | 413 |  | 37% |  | 99.5% |  | 91.8% |  | 7.1 |  | 0 |  | 2.2
|  | MIL01-07-13 |  | 402 |  | 36% |  | 99.7% |  | 96% |  | 5.8 |  | 0 |  | 1.1
|  | MIL01-07-14 |  | 397 |  | 35.6% |  | 99.5% |  | 93.9% |  | 6.8 |  | 0 |  | 2
|  | Turbine Averages |  | 391.3846 |  | 34.98% |  | 97.43% |  | 93.01% |  | 6.6359 |  | 0 |  | 10.0385
|  | Site Totals |  | 15265 |  | 35.1% |  | 97.5% |  | 93.1% |  | 6.6359 |  | 0 |  | 391.6

## Table lost energy_1
185 | 94 |  | 67 | 185 | 94 | -1
5.2 Lost Energy
Table 5.2(a) Lost Energy
+ | + | -
Offline Lost Energy |  | +
+
Category | Lost Energy (MWh) | +
Environmental | 5.0893 | + |  |  |  |  | formatting
Environmental - Icing | 0 | + | note: "not categorized" is manually moved to "manufacturer - fault" |  |  |  | Row height | 15
Manufacturer - Fault | 149.5345 | +
Manufacturer - Blade Repair | 0 | +
Manufacturer - Gearbox | 0 | +
Manufacturer - Generator | 0 | +
Manufacturer - Planned Maintenance | 237.129 | +
Manufacturer - Other | 0 | +
Not Categorized | 0 | +
Owner | 0 | + |  | Notes to add below waterfall chart:
Owner - Repair | 0 | + |  | Budget energy: | Modeled energy based on planned wind resource and planned losses
Utility/BOP | 0 | + |  | Budget adjustment categories: | Effective gain due to budgeted losses which have no corresponding actual measureable losses
Environmental - Bird/Bat | 0 | + |  | Year 1 availability | Budgeted additional losses expected in year 1
Total | 391.7528 | + |  | Budget wake effect adj.: | Deep array wake model effects used in budget are higher than actual
|  |  |  | Resource adjustment: | Difference between predicted energy (using actual wind resource) and budget energy plus budget adjustments (using planned wind resource)
|  |  |  | Predicted energy: | Based on modeled power curves, actual wind resource, and planned measureable losses
Lost energy waterfall |  |  |  | Measureable turbine loss categories: | Difference between budgeted losses and corresponding measured losses due to turbine downtime (positive if actual loss is smaller than budgeted loss)
|  |  |  | Line loss category: | Difference between budgeted line loss and corresponding measured transmission line losses between turbines and meter
Totals |  |  |  | "Other" category: | Any additional uncategorized loss or gain
Gross budget energy (P50) | 29209.0191 |  |  | Actual energy: | Actual energy measured at the meter
Budget energy (P50) | 22899.871
Turbine energy export | 25039.472
Actual net meter/invoiced energy | 24224.578
Resource adjustment
Budget wind speed | 7.83
Actual wind speed | 7.923
Energy loss/gain
Category | Actual MWh | Budgeted | Actual minus Budget MWh | Waterfall MWh | Notes
Budget Energy | 22899.871 |  | 22899.871 | 22899.871
Budget DAWM Adj. |  | 1168.3608 | 1168.3608 | 1168.3608
Adjusted Budget Energy | 24068.2318 |  | 24068.2318
Resource Adjustment | 3397.8194 |  | -639.6902 | -639.6902
Predicted | 27466.0511 |  | 23428.5416 | 23428.5416 | From turbine wind speed using turbine power curve
Budget Wake Effects |  | -631.7192
Budget Turbine Performance Adj. |  | -604.2531
Budget Blade Degradation |  | -247.1945
Icing | -149.5345 | -274.6605 | 125.126 | 125.126
Environmental | 0 | -82.3982 | 82.3982 | 82.3982
Manufacturer - Blade Repair | 0 | 0 | 0 | 0
Manufacturer - Gearbox | 0 | 0 | 0 | 0
Manufacturer - Generator | 0 | 0 | 0 | 0
Manufacturer - PM | -237.129 | -686.6513 | 449.5223 | 449.5223
Manufacturer - Other | 0 | 0 | 0 | 0
Not Categorized | 0 | 0 | 0 | 0
Owner | 0 | -178.5293 | 178.5293 | 178.5293
Owner - Repair | 0 | -178.5293 | 178.5293 | 178.5293
Utility/BOP | 0 | -178.5293 | 178.5293 | 178.5293
Environmental - Bird/Bat | 0 | -178.5293 | 178.5293 | 178.5293
Economic Curtailment | -5.0893 | -851.4476 | 846.3583 | 846.3583
Line Loss | -814.894 | -576.7871 | -238.1069 | -238.1069
Other | -2034.8263 |  | -1183.3787 | -1183.3787 | Other losses/gains may be attributed to differences between budgeted and actual turbine performance compared to power curve and blade degradation, as well as error in resource adjustment
Actual Net Meter Energy | 24224.578 |  | 24224.578 | 24224.578
Budget losses
Curtailment | 3.1%
Blade degradation | 0.9%
Environmental - Icing | 1%
Environmental | 0.3%
Contractual turbine availability | 2.5%
Non-contractual turbine availability | 2.6% | Non-contractual turbine avail plus high-wind correlated avail in AWS resource assessment
Grid availability | 0.6%
Turbine performance | 2.2%
Wake and blocking effects | 6.3%
Blocking effects (between turbines) | 2.1%
Deep array wake effects | 4%
Bull Hill project wake effects | 0.2%
Year 1 project avail | 0%
Line loss | 2.1%
Total in budget | 21.6%
Total expected | 21.6%
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.

## Table lost energy ytd
YTD Energy Waterfall |  | Lost energy in units of MWh
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| Category | January | February | March | April | May | June | July | August | September | October | November | December | YTD
Actual Energy
| Meter net energy | 22185.555 | 16838.995 | 29746.721 | 20841.72 | 17271.181 | 17003.132 | 10830.961 | 7319.614 | 16027.069 | 16032.604 | 21162.889 | 24224.578 | 219485.019
| Meter export energy | 22236.792 | 16898.126 | 29749.919 | 20877.009 | 17339.737 | 17035.096 | 10930.305 | 7445.264 | 16102.786 | 16089.272 | 21200.957 | 24260.434 | 220165.697
| Turbine export energy | 22918.8312 | 17495.8528 | 30630.208 | 21498.698 | 17873.665 | 17541.457 | 11310.103 | 7758.472 | 16609.632 | 16596.274 | 21863.933 | 25039.472 | 227136.598
Predicted Energy
| Predicted turbine export energy (gross) | 25327.387 | 21587.0447 | 33420.1821 | 24692.2568 | 19912.1026 | 17572.5425 | 13213.9704 | 8069.8661 | 15679.1698 | 17112.2281 | 23750.5525 | 27466.0511 | 247803.3535
| Predicted meter export energy | 21319.6687 | 18171.1853 | 28131.8879 | 20785.0394 | 16761.2803 | 14791.924 | 11123.0373 | 6792.9183 | 13198.1521 | 14404.4482 | 20111.0999 | 23257.2483 | 208847.8897
Actual Losses
| Economic Curtailment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environmental | 5.1527 | 0.46635 | 2.5682 | 2.9102 | 6.0853 | 1.9048 | 1.4844 | 1.5663 | 6.661 | 1.8347 | 0.51846 | 5.0893 | 36.2419
| Environmental - Bird/Bat | 0 | 0 | 0 | 143.1303 | 1797.0243 | 1514.5564 | 1910.0023 | 2726.0274 | 1822.4629 | 0 | 0 | 0 | 9913.2036
| Environmental - Icing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Manufacturer - Fault | 1096.7789 | 873.9393 | 122.7991 | 214.8318 | 200.8727 | 138.4181 | 25.9564 | 25.5963 | 86.5983 | 158.0869 | 116.6067 | 149.5345 | 3210.0189
| Manufacturer - Blade Repair | 0 | 0 | 0 | 0 | 0 | 0 | 1.1449 | 0 | 0 | 0 | 0 | 0 | 1.1449
| Manufacturer - Gearbox | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Manufacturer - Generator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Manufacturer - Planned Maintenance | 132.9418 | 110.6544 | 286.5067 | 203.9063 | 54.678 | 3.7132 | 11.4636 | 0.62628 | 12.0661 | 180.1827 | 171.1923 | 237.129 | 1405.0605
| Manufacturer - Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Not Categorized | 110.322 | 20.6883 | 0.51423 | 2.1762 | 0 | 0.08565 | 0.88997 | 0 | 0 | 9.4827 | 0.40692 | 0 | 144.5659
| Owner | 0 | 0 | 22.3422 | 126.5973 | 659.5413 | 0 | 2.1861 | 0.2499 | 0 | 0 | 0 | 0 | 810.9169
| Owner - Repair | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1327 | 0 | 0 | 9.1327
| Utility/BOP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0076373 | 7.9896 | 0 | 0 | 0 | 7.9972
| Line Loss | 682.0392 | 597.7268 | 880.289 | 621.689 | 533.928 | 506.361 | 379.798 | 313.208 | 506.846 | 507.002 | 662.976 | 779.038 | 6970.901
Budget Energy
| Budget meter net energy (gross) | 31551.0488 | 28385.6889 | 31766.6361 | 26809.4633 | 21168.5314 | 17707.0343 | 15662.4609 | 14638.8949 | 19382.4501 | 27972.2362 | 26719.0042 | 29217.8347 | 290981.2835
| Budget meter net energy | 23466.517 | 21112.238 | 23626.863 | 19939.899 | 15744.38 | 13169.845 | 11649.166 | 10887.875 | 14415.958 | 20804.727 | 20941.379 | 22899.871 | 218658.718
Budget Losses (no expected actual)
| Year 1 Availability | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 0% | 0%
|  | 1104.2867 | 993.4991 | 1111.8323 | 938.3312 | 740.8986 | 619.7462 | 548.1861 | 512.3613 | 678.3858 | 979.0283 | 0 | 0 | 8226.5556
| Wake Effects (DAWM) | 3.2% | 3.2% | 3.2% | 3.2% | 3.2% | 3.2% | 3.2% | 3.2% | 3.2% | 3.2% | 3.2% | 3.2%
|  | 1009.6336 | 908.342 | 1016.5324 | 857.9028 | 677.393 | 566.6251 | 501.1987 | 468.4446 | 620.2384 | 895.1116 | 855.0081 | 934.9707 | 9311.4011
Budget Losses (expected actual, non-measureable)
| Budget Blocking + Wake Effects | 3.1% | 3.1% | 3.1% | 3.1% | 3.1% | 3.1% | 3.1% | 3.1% | 3.1% | 3.1% | 3.1% | 3.1%
|  | 785.149 | 669.1984 | 1036.0256 | 765.46 | 617.2752 | 544.7488 | 409.6331 | 250.1658 | 486.0543 | 530.4791 | 736.2671 | 851.4476 | 7681.904
| Budget Turbine Performance Adj. | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% | 2.2%
|  | 557.2025 | 474.915 | 735.244 | 543.2296 | 438.0663 | 386.5959 | 290.7073 | 177.5371 | 344.9417 | 376.469 | 522.5122 | 604.2531 | 5451.6738
| Budget Blade Degradation | 0.4% | 0.4% | 0.4% | 0.4% | 0.4% | 0.4% | 0.4% | 0.4% | 0.4% | 0.4% | 0.9% | 0.9%
|  | 101.3095 | 86.3482 | 133.6807 | 98.769 | 79.6484 | 70.2902 | 52.8559 | 32.2795 | 62.7167 | 68.4489 | 213.755 | 247.1945 | 1247.2964
| Budget Directional Curtail. | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5%
|  | 126.6369 | 107.9352 | 167.1009 | 123.4613 | 99.5605 | 87.8627 | 66.0699 | 40.3493 | 78.3958 | 85.5611 | 118.7528 | 137.3303 | 1239.0168
Budget Losses (expected actual, measureable)
| Environmental - Bird/Bat | 2.6% | 2.6% | 2.6% | 2.6% | 2.6% | 2.6% | 2.6% | 2.6% | 2.6% | 2.6% | 2.6% | 2.6%
|  | 658.5121 | 561.2632 | 868.9247 | 641.9987 | 517.7147 | 456.8861 | 343.5632 | 209.8165 | 407.6584 | 444.9179 | 617.5144 | 714.1173 | 6442.8872
Environmental - Icing | bar: Lost energy in units of MWh 1 January to Lost energy in units of MWh 12 December
|  | 253.2739 | 215.8704 | 334.2018 | 246.9226 | 199.121 | 175.7254 | 132.1397 | 80.6987 | 156.7917 | 171.1223 | 237.5055 | 274.6605 | 2478.0335
| Environmental | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3%
|  | 75.9822 | 64.7611 | 100.2605 | 74.0768 | 59.7363 | 52.7176 | 39.6419 | 24.2096 | 47.0375 | 51.3367 | 71.2517 | 82.3982 | 743.4101
| Contractual turbine availability | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 2.5% | 2.5%
|  | 886.4585 | 755.5466 | 1169.7064 | 864.229 | 696.9236 | 615.039 | 462.489 | 282.4453 | 548.7709 | 598.928 | 593.7638 | 686.6513 | 8160.9513
| Non-contractual turbine availability | 2.6% | 2.6% | 2.6% | 2.6% | 2.6% | 2.6% | 2.6% | 2.6% | 2.6% | 2.6% | 2.6% | 2.6%
|  | 658.5121 | 561.2632 | 868.9247 | 641.9987 | 517.7147 | 456.8861 | 343.5632 | 209.8165 | 407.6584 | 444.9179 | 617.5144 | 714.1173 | 6442.8872
| Grid availability | 0.6237% | 0.6237% | 0.6237% | 0.6237% | 0.6237% | 0.6237% | 0.6237% | 0.6237% | 0.6237% | 0.6237% | 0.6237% | 0.6237%
|  | 157.9554 | 134.6286 | 208.4265 | 153.9944 | 124.1827 | 109.592 | 82.4095 | 50.3281 | 97.7839 | 106.7212 | 148.1214 | 171.2933 | 1545.4371
| Line loss | 2.1% | 2.1% | 2.1% | 2.1% | 2.1% | 2.1% | 2.1% | 2.1% | 2.1% | 2.1% | 2.1% | 2.1%
|  | 531.8751 | 453.3279 | 701.8238 | 518.5374 | 418.1542 | 369.0234 | 277.4934 | 169.4672 | 329.2626 | 359.3568 | 498.7616 | 576.7871 | 5203.8704
PPA Curtailment | bar: Lost energy in units of MWh 1 January to Lost energy in units of MWh 12 December
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Budget Losses (total, project) | 25.62% | 25.62% | 25.62% | 25.62% | 25.62% | 25.62% | 25.62% | 25.62% | 25.62% | 25.62% | 21.62% | 21.62%
Wind Speeds (for reference)
| Budget wind speed | 8.1 | 8.14 | 8.3 | 7.48 | 6.65 | 6.26 | 5.89 | 5.88 | 6.58 | 7.47 | 7.64 | 7.83 | 7.185
| Actual wind speed | 7.3456 | 7.2773 | 8.9502 | 7.5803 | 6.6129 | 6.6986 | 5.6822 | 5.0678 | 6.5263 | 6.6201 | 7.2239 | 7.923 | 6.959
| Waterfall buckets | January | February | March | April | May | June | July | August | September | October | November | December | YTD | Note: % versions below chart
| Budget Energy | 23466.517 | 21112.238 | 23626.863 | 19939.899 | 15744.38 | 13169.845 | 11649.166 | 10887.875 | 14415.958 | 20804.727 | 20941.379 | 22899.871 | 218658.718
| Budget Year 1 Avail. Adj | 1104.2867 | 993.4991 | 1111.8323 | 938.3312 | 740.8986 | 619.7462 | 548.1861 | 512.3613 | 678.3858 | 979.0283 | 0 | 0 | 8226.5556
| Budget Wake Effect Adj. | 1009.6336 | 908.342 | 1016.5324 | 857.9028 | 677.393 | 566.6251 | 501.1987 | 468.4446 | 620.2384 | 895.1116 | 855.0081 | 934.9707 | 9311.4011
| Adjusted Budget Energy | 25580.4373 | 23014.0792 | 25755.2276 | 21736.133 | 17162.6716 | 14356.2163 | 12698.5509 | 11868.681 | 15714.5822 | 22678.8668 | 21796.3871 | 23834.8417 | 236196.6746
| Resource Adjustment | -4260.7685 | -4842.8939 | 2376.6603 | -951.0937 | -401.3913 | 435.7077 | -1575.5136 | -5075.7626 | -2516.43 | -8274.4186 | -1685.2872 | -577.5934 | -27348.7849
| Predicted Energy | 21319.6687 | 18171.1853 | 28131.8879 | 20785.0394 | 16761.2803 | 14791.924 | 11123.0373 | 6792.9183 | 13198.1521 | 14404.4482 | 20111.0999 | 23257.2483 | 208847.8897
| Bird/Bat Curtailment | 658.5121 | 561.2632 | 868.9247 | 498.8684 | -1279.3096 | -1057.6703 | -1566.4391 | -2516.2109 | -1414.8045 | 444.9179 | 617.5144 | 714.1173 | -3470.3164
| Icing | 253.2739 | 215.8704 | 334.2018 | 246.9226 | 199.121 | 175.7254 | 132.1397 | 80.6987 | 156.7917 | 171.1223 | 237.5055 | 274.6605 | 2478.0335
| Environmental | 70.8294 | 64.2948 | 97.6923 | 71.1665 | 53.651 | 50.8128 | 38.1575 | 22.6433 | 40.3765 | 49.502 | 70.7332 | 77.3088 | 707.1682
| Manufacturer - Fault | -306.153 | -203.3055 | 228.1338 | 228.5572 | 346.9361 | 460.553 | 285.3249 | 250.1033 | 395.0609 | 121.816 | 123.9669 | 116.0144 | 2047.0079
| Manufacturer - Blade Repair | 0 | 0 | 0 | 0 | 0 | 0 | 12.5858 | 0 | 0 | 0 | 0 | 0 | 12.5858
| Manufacturer - Gearbox | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Manufacturer - Generator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Manufacturer - PM | -37.1092 | -25.7417 | 532.2667 | 216.9337 | 94.4368 | 12.3547 | 126.0132 | 6.1195 | 55.0457 | 138.8423 | 181.998 | 183.9734 | 1485.1333
| Manufacturer - Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Not Categorized | 548.1901 | 540.5749 | 19.0352 | 8.6732 | 0 | 456.8005 | 98.5096 | 0 | 135.8861 | 217.1591 | 617.1074 | 238.0391 | 2879.9752
| Owner | 0 | 0 | 827.0331 | 504.552 | -141.8267 | 0 | 241.9775 | 209.5666 | 135.8861 | 0 | 0 | 238.0391 | 2015.2278
| Owner - Repair | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135.8861 | 209.1435 | 0 | 238.0391 | 583.0687
| Utility/BOP | 157.9554 | 134.6286 | 208.4265 | 153.9944 | 124.1827 | 109.592 | 82.4095 | 50.3205 | 89.7943 | 106.7212 | 148.1214 | 171.2933 | 1537.4399
| Economic Curtailment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Line Loss | -150.1641 | -144.3988 | -178.4652 | -103.1516 | -115.7738 | -137.3376 | -102.3046 | -143.7408 | -177.5834 | -147.6452 | -164.2144 | -202.2509 | -1767.0306
| Other | -329.4483 | -2475.3761 | -1322.4159 | -1769.8358 | 1228.4832 | 2140.3775 | 359.5496 | 2567.1956 | 3276.5773 | 316.5767 | -780.9433 | -1081.9045 | 2128.8359
| Actual Net Meter Energy | 22185.555 | 16838.995 | 29746.721 | 20841.72 | 17271.181 | 17003.132 | 10830.961 | 7319.614 | 16027.069 | 16032.604 | 21162.889 | 24224.578 | 219485.019
| Waterfall buckets (% from prev. total) | January | February | March | April | May | June | July | August | September | October | November | December | YTD
| Budget Energy | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| Budget Year 1 Avail. Adj | 4.706% | 4.706% | 4.706% | 4.706% | 4.706% | 4.706% | 4.706% | 4.706% | 4.706% | 4.706% | 0% | 0% | 3.762%
| Budget Wake Effect Adj. | 4.302% | 4.302% | 4.302% | 4.302% | 4.302% | 4.302% | 4.302% | 4.302% | 4.302% | 4.302% | 4.083% | 4.083% | 4.258%
| Adjusted Budget Energy | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| Resource Adjustment | -16.66% | -21.04% | 9.228% | -4.376% | -2.339% | 3.035% | -12.41% | -42.77% | -16.01% | -36.49% | -7.732% | -2.423% | -11.58%
| Predicted Energy | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| Bird/Bat Curtailment | 3.089% | 3.089% | 3.089% | 2.4% | -7.633% | -7.15% | -14.08% | -37.04% | -10.72% | 3.089% | 3.071% | 3.071% | -1.662%
| Icing | 1.188% | 1.188% | 1.188% | 1.188% | 1.188% | 1.188% | 1.188% | 1.188% | 1.188% | 1.188% | 1.181% | 1.181% | 1.187%
| Environmental | 0.3322% | 0.3538% | 0.3473% | 0.3424% | 0.3201% | 0.3435% | 0.343% | 0.3333% | 0.3059% | 0.3437% | 0.3517% | 0.3324% | 0.3386%
| Manufacturer - Fault | -1.436% | -1.119% | 0.8109% | 1.1% | 2.07% | 3.114% | 2.565% | 3.682% | 2.993% | 0.8457% | 0.6164% | 0.4988% | 0.9801%
| Manufacturer - Blade Repair | 0% | 0% | 0% | 0% | 0% | 0% | 0.1132% | 0% | 0% | 0% | 0% | 0% | 0.006026%
| Manufacturer - Gearbox | [12 empty] | 0% | bar: January to December
| Manufacturer - Generator | [12 empty] | 0% | bar: January to December
| Manufacturer - PM | -0.1741% | -0.1417% | 1.892% | 1.044% | 0.5634% | 0.08352% | 1.133% | 0.09009% | 0.4171% | 0.9639% | 0.905% | 0.791% | 0.7111%
| Manufacturer - Other | [12 empty] | 0% | bar: January to December
| Not Categorized | 2.571% | 2.975% | 0.06766% | 0.04173% | 0% | 3.088% | 0.8856% | 0% | 1.03% | 1.508% | 3.068% | 1.024% | 1.379%
| Owner | 0% | 0% | 2.94% | 2.427% | -0.8462% | 0% | 2.175% | 3.085% | 1.03% | 0% | 0% | 1.024% | 0.9649%
| Owner - Repair | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.03% | 1.452% | 0% | 1.024% | 0.2792%
| Utility/BOP | 0.7409% | 0.7409% | 0.7409% | 0.7409% | 0.7409% | 0.7409% | 0.7409% | 0.7408% | 0.6804% | 0.7409% | 0.7365% | 0.7365% | 0.7362%
| Economic Curtailment | [12 empty] | 0% | bar: January to December
| Line Loss | -0.7043% | -0.7947% | -0.6344% | -0.4963% | -0.6907% | -0.9285% | -0.9198% | -2.116% | -1.346% | -1.025% | -0.8165% | -0.8696% | -0.8461%
| Other | -1.545% | -13.62% | -4.701% | -8.515% | 7.329% | 14.47% | 3.232% | 37.79% | 24.83% | 2.198% | -3.883% | -4.652% | 1.019%
| Actual Net Meter Energy | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
Note on B40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assuming 20% of DAWM effects are accurate and putting these under Budget Blocking + Wake Effects instead
Note on B44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Applies to gross budget but not to gross predicted

## Table lost energy_2
185 | 94 | 67 | 185 | 94 |  | -1
Table 6.2(b) Lost Energy
Offline Lost Energy |  |  | Curtailment Lost Energy
Category | Lost Energy (MWh) |  | Category | Lost Energy (MWh)
BOP-Fault | 0 |  | CRT-Bearing | 0 | +
BOP-Maintenance | 0 |  | CRT-Bird/Bat | 0 | +
BOP-Other | 0 |  | CRT-Blade | 0 | +
ENV-Bird/Bat | 12.2 |  | CRT-Gearbox | 0 | +
ENV-Icing | 0 |  | CRT-Icing | 0 | +
ENV-Other | 0 |  | CRT-Offtaker | 0 | +
Environmental | 0 |  | CRT-Other | 0 | +
FTH-Fault | 353 |  | Total | 0 | +
Other | 0 |  |  |  | +
PTH-Maintenance | 23.4 |  |  |  | +
PTH-Retrofit | 0 |  |  |  | +
REP-Bearing | 0 |  |  |  | +
REP-Blade | 0 |  |  |  | +
REP-Gearbox | 0 |  |  |  | +
REP-Generator | 0 |  |  |  | +
REP-Other | 0 |  |  |  | +
TCH-Normal | 3 |  |  |  | +
Utility | 0 |  |  |  | +
Total | 391.6 |  |  |  | +

## Table fault_1
| 50 | 295 | 84 | 71 | 113 | [5 empty] | 11
6.4 Turbine Faults
Table 6.4(a) Top 12 Turbine Fault and Event States by Lost Energy
| + | + | + | + | + | -
| Code | Fault | Count: Faults | RTS Hours | Lost Energy (MWh) | Count: Turbines Impacted |  | Period Hours | Mean Time To Repair | Mean Time Between Faults | Cumulative | % of total
| 900 | Pause pressed on keyboard | 59 | 150.9281 | 237.129 | 22 | + | 16368 | 2.5581 | 274.8656 | 237.129 | 60.53% | Pause pressed on key…
| 5179 | Fire cylinder gas level low | 2 | 260.4089 | 69.099 | 1 | + | 16368 | 130.2044 | 8053.7956 | 306.228 | 78.17% | Fire cylinder gas le…
| 3719 | TowAcc Y,Extreme: m/s^ | 34 | 4.4142 | 18.4519 | 15 | + | 16368 | 0.12983 | 481.2819 | 324.68 | 82.88% | TowAcc Y,Extreme: m/…
| 110 | Boat action curtailment | 222 | 264.8333 | 17.956 | 22 | + | 16368 | 1.1929 | 72.5368 | 342.636 | 87.46% | Boat action curtailm…
| 309 | Pause over RCS | 191 | 23.2544 | 15.9655 | 11 | + | 16368 | 0.12175 | 85.5746 | 358.6015 | 91.54% | Pause over RCS …
| 5101 | HiTempChokeWind:Mod; °C | 14 | 3.5236 | 14.1642 | 1 | + | 16368 | 0.25169 | 1168.8912 | 372.7656 | 95.15% | HiTempChokeWind:Mod;…
| 296 | Tow. acc. X,Alarm: m/s^ | 14 | 5.1444 | 14.1077 | 1 | + | 16368 | 0.36746 | 1168.7754 | 386.8733 | 98.75% | Tow. acc. X,Alarm: m…
| 4518 | HubSafty HydrPres Low BldC | 3 | 2.2661 | 6.3339 | 3 | + | 16368 | 0.75537 | 5455.2446 | 393.2072 | 100.4% | HubSafty HydrPres Lo…
| 3234 | PitchAccumulatorTestAccFailed | 2 | 1.4492 | 3.5616 | 1 | + | 16368 | 0.72458 | 8183.2754 | 396.7687 | 101.3% | PitchAccumulatorTest…
| 356 | Extreme yawerror m/s° | 16 | 0.5225 | 2.6488 | 12 | + | 16368 | 0.032656 | 1022.9673 | 399.4175 | 102% | Extreme yawerror m/s…
| 3273 | YawUntwistCCW: Code,° | 89 | 32.2503 | 2.4157 | 22 | + | 16368 | 0.36236 | 183.5477
| 4517 | HubSafty HydrPres Low BldB | 3 | 0.54028 | 1.7875 | 3 | + | 16368 | 0.18009 | 5455.8199
0

## Table fault_2
| 50 | 229 | 121 | 111 | 113
Table 6.4(b) Top 12 Turbine Fault and Event States by Lost Energy Milford 1 GE
| Code | Fault | Count | Hours | Lost Energy (MWh)
| 147 | Load shutdown | 927 | 87 | 28
| 102 | Motor protection top cabinet | 1 | 47 | 19
| 62 | Plc fault collection | 1 | 16 | 17
| 274 | Pitch thyristor 1 fault | 28 | 64 | 9
| 135 | Emergency braking system test | 129 | 44 | 6
| 122 | Collective fault pitch controller | 41 | 12 | 6
| 150 | Axis 3 fault pitch controller | 1 | 1 | 1
| 121 | Axis 1 fault pitch controller | 7 | 1 | 1
| 276 | Pitch thyristor 3 fault | 5 | 1 | 1
| 38 | Secondary brake test | 22 | 1 | 1
| 21 | Cable twisting left | 38 | 45 | 0
| 105 | Generator side ccu fault voltage | 1 | 3 | 0
0

## Figure daily wind
daily availability
site | Timestamp | Capacity factor | Data Availability | Energy Budget - Default | Energy Export |  | Production-based Contractual Avail. | Time-based Contractual Avail. | Wind speed | Day | Availability | BOP | PTH | FTH/REP | total
Milford 2 GE | 2020-10-01 | 0.061705 | 0.98928 | 420604.8387 | 125171 |  | 0.98724 | 0.90384 | 3.4202 | 1 | 98.724 | 0 |  | 1.276 | 100
Milford 2 GE | 2020-10-02 | 0.030313 | 1 | 420604.8387 | 62646 |  | 0.99208 | 0.9182 | 2.7729 | 2 | 99.2085 | 0 |  | 0.79153 | 100
Milford 2 GE | 2020-10-03 | 0.04682 | 0.99829 | 420604.8387 | 96595.3205 |  | 0.99247 | 0.92944 | 3.1532 | 3 | 99.2472 | 0 |  | 0.75278 | 100
Milford 2 GE | 2020-10-04 | 0.0023343 | 0.98233 | 420604.8387 | 6237.8685 |  | 0.99438 | 0.91275 | 1.9045 | 4 | 99.4381 | 0 |  | 0.56185 | 100
Milford 2 GE | 2020-10-05 | 0.074613 | 0.98233 | 420604.8387 | 152382.8685 |  | 0.98423 | 0.89719 | 4.0898 | 5 | 98.4227 | 0 |  | 1.5773 | 100
Milford 2 GE | 2020-10-06 | 0.034399 | 0.99245 | 420604.8387 | 70727.9425 |  | 0.99128 | 0.91272 | 2.6544 | 6 | 99.128 | 0 |  | 0.87199 | 100
Milford 2 GE | 2020-10-07 | 0.039238 | 0.98294 | 420604.8387 | 79096 |  | 0.99327 | 0.91034 | 2.6175 | 7 | 99.3268 | 0 |  | 0.67319 | 100
Milford 2 GE | 2020-10-08 | 0.21434 | 0.99622 | 420604.8387 | 440388.3878 |  | 0.98374 | 0.91468 | 6.1135 | 8 | 98.374 |  |  | 1.626 | 100
Milford 2 GE | 2020-10-09 | 0.27332 | 0.99781 | 420604.8387 | 560765.6122 |  | 0.98409 | 0.91279 | 6.6226 | 9 | 98.4086 |  | 0.79569 | 0.79569 | 100
Milford 2 GE | 2020-10-10 | 0.41095 | 0.99988 | 420604.8387 | 843427 |  | 0.98424 | 0.92219 | 7.4949 | 10 | 98.4242 |  | 0.78789 | 0.78789 | 100
Milford 2 GE | 2020-10-11 | 0.53313 | 1 | 420604.8387 | 1094311 |  | 0.9658 | 0.89448 | 8.6122 | 11 | 96.5798 |  | 1.0261 | 2.3942 | 100
Milford 2 GE | 2020-10-12 | 0.056117 | 0.99817 | 420604.8387 | 115664.9114 |  | 0.99131 | 0.91939 | 3.7468 | 12 | 99.131 |  | 0.43449 | 0.43449 | 100
Milford 2 GE | 2020-10-13 | 0.080931 | 0.9922 | 420604.8387 | 166703.0886 |  | 0.99028 | 0.9185 | 4.2343 | 13 | 99.0282 |  | 0.48592 | 0.48592 | 100
Milford 2 GE | 2020-10-14 | 0.27064 | 0.99988 | 420604.8387 | 555912 |  | 0.99168 | 0.91367 | 6.3693 | 14 | 99.1685 |  | 0.41576 | 0.41576 | 100
Milford 2 GE | 2020-10-15 | 0.3696 | 0.99318 | 420604.8387 | 755907 |  | 0.99006 | 0.91585 | 7.4895 | 15 | 99.006 |  | 0.49699 | 0.49699 | 100
Milford 2 GE | 2020-10-16 | 0.13123 | 0.99988 | 420604.8387 | 269876 |  | 0.99362 | 0.90719 | 4.629 | 16 | 99.3625 |  | 0.31876 | 0.31876 | 100
Milford 2 GE | 2020-10-17 | 0.070397 | 0.99196 | 420604.8387 | 143272 |  | 0.98921 | 0.91341 | 3.5688 | 17 | 98.9211 | 0.21579 |  | 0.86316 | 100
Milford 2 GE | 2020-10-18 | 0.011747 | 1 | 420604.8387 | 24874 |  | 0.98537 | 0.91062 | 2.3674 | 18 | 98.5374 | 0.29252 |  | 1.1701 | 100
Milford 2 GE | 2020-10-19 | 0.04349 | 1 | 420604.8387 | 89611 |  | 0.99238 | 0.9082 | 2.7283 | 19 | 99.2382 | 0.15235 |  | 0.6094 | 100
Milford 2 GE | 2020-10-20 | 0.014418 | 0.99464 | 420604.8387 | 30288 |  | 0.96168 | 0.88462 | 2.1111 | 20 | 96.1677 | 0.76646 |  | 3.0658 | 100
Milford 2 GE | 2020-10-21 | 0.33249 | 0.99208 | 420604.8387 | 672589 |  | 0.97329 | 0.90318 | 6.0273 | 21 | 97.3294 | 0.53411 |  | 2.1364 | 100
Milford 2 GE | 2020-10-22 | 0.55581 | 0.98063 | 420604.8387 | 1120233 |  | 0.97136 | 0.89748 | 8.6922 | 22 | 97.1363 | 0.57275 |  | 2.291 | 100
Milford 2 GE | 2020-10-23 | 0.13932 | 0.9933 | 420604.8387 | 285938 |  | 0.99881 | 0.91913 | 4.4291 | 23 | 99.8807 | 0.023856 |  | 0.095424 | 100
Milford 2 GE | 2020-10-24 | 0.69483 | 0.99586 | 420604.8387 | 1424993 |  | 0.97343 | 0.90939 | 9.8059 | 24 | 97.3433 | 0.53134 |  | 2.1254 | 100
Milford 2 GE | 2020-10-25 | 0.58355 | 0.99939 | 420604.8387 | 1197528 |  | 0.94798 | 0.8596 | 8.9098 | 25 | 94.7976 | 1.0405 |  | 4.162 | 100
Milford 2 GE | 2020-10-26 | 0.41448 | 1 | 420604.8387 | 850675 |  | 0.96183 | 0.88166 | 7.5967 | 26 | 96.1834 | 0.76333 |  | 3.0533 | 100
Milford 2 GE | 2020-10-27 | 0.21618 | 0.99659 | 420604.8387 | 443171 |  | 0.9687 | 0.88652 | 6.0223 | 27 | 96.8698 | 0.62603 |  | 2.5041 | 100
Milford 2 GE | 2020-10-28 | 0.092506 | 1 | 420604.8387 | 190308 |  | 0.98355 | 0.90686 | 4.0956 | 28 | 98.355 | 0.329 |  | 1.316 | 100
Milford 2 GE | 2020-10-29 | 0.02692 | 0.99939 | 420604.8387 | 55903 |  | 0.98203 | 0.90412 | 2.5143 | 29 | 98.2026 | 0.35948 |  | 1.4379 | 100
Milford 2 GE | 2020-10-30 | 0.0081835 | 0.98745 | 420604.8387 | 17390 |  | 0.99427 | 0.90896 | 2.202 | 30 | 99.4265 | 0.11469 |  | 0.45877 | 100
Milford 2 GE | 2020-10-31 | 0.13797 | 0.99988 | 420604.8387 | 283368 |  | 0.98565 | 0.88722 | 4.7875 | 31 | 98.565 | 0.28699 |  | 1.148 | 100
[5 empty] | timestamp | day | Wind speed | Project availability | Energy Export (MWh) | Project Lost Energy (MWh)
[5 empty] | 2021-12-01 | 1 | 5.2113 | 0.96991 | 309.506 | 9.6015
[5 empty] | 2021-12-02 | 2 | 9.0669 | 0.96607 | 1166.517 | 40.9699
[5 empty] | 2021-12-03 | 3 | 12.7018 | 0.99575 | 1552.859 | 6.6274
[5 empty] | 2021-12-04 | 4 | 5.7317 | 0.99976 | 445.284 | 0.10694
[5 empty] | 2021-12-05 | 5 | 6.8902 | 0.99971 | 656.298 | 0.18853
[5 empty] | 2021-12-06 | 6 | 13.3929 | 0.95642 | 1497.628 | 68.2349
[5 empty] | 2021-12-07 | 7 | 9.5433 | 0.97673 | 1132.691 | 26.9876
[5 empty] | 2021-12-08 | 8 | 6.3117 | 0.99332 | 514.088 | 3.4595
[5 empty] | 2021-12-09 | 9 | 6.6451 | 0.99093 | 535.453 | 4.8992
[5 empty] | 2021-12-10 | 10 | 5.3271 | 0.97144 | 295.377 | 8.6845
[5 empty] | 2021-12-11 | 11 | 9.9533 | 0.99986 | 1146.712 | 0.16575
[5 empty] | 2021-12-12 | 12 | 12.8009 | 0.99967 | 1627 | 0.53228
[5 empty] | 2021-12-13 | 13 | 9.5901 | 0.98432 | 1217.759 | 19.3956
[5 empty] | 2021-12-14 | 14 | 10.4844 | 0.97416 | 1345.228 | 35.6869
[5 empty] | 2021-12-15 | 15 | 5.7092 | 0.99869 | 470.775 | 0.61754
[5 empty] | 2021-12-16 | 16 | 7.373 | 0.99844 | 782.197 | 1.2232
[5 empty] | 2021-12-17 | 17 | 11.3716 | 0.98684 | 1519.733 | 20.2631
[5 empty] | 2021-12-18 | 18 | 6.0012 | 0.99875 | 494.609 | 0.61671
[5 empty] | 2021-12-19 | 19 | 7.3796 | 0.99937 | 688.499 | 0.43587
[5 empty] | 2021-12-20 | 20 | 6.4104 | 0.99696 | 584.332 | 1.78
[5 empty] | 2021-12-21 | 21 | 7.6063 | 0.9996 | 823.826 | 0.3309
[5 empty] | 2021-12-22 | 22 | 11.0204 | 0.98651 | 1152.665 | 15.7621
[5 empty] | 2021-12-23 | 23 | 12.3216 | 0.9776 | 1356.347 | 31.0786
[5 empty] | 2021-12-24 | 24 | 9.2461 | 0.99985 | 1167.14 | 0.17953
[5 empty] | 2021-12-25 | 25 | 5.6392 | 0.99704 | 407.107 | 1.2096
[5 empty] | 2021-12-26 | 26 | 6.588 | 0.95242 | 568.375 | 28.3973
[5 empty] | 2021-12-27 | 27 | 7.1341 | 0.95575 | 700.215 | 32.416
[5 empty] | 2021-12-28 | 28 | 6.3736 | 0.94444 | 526.168 | 30.9544
[5 empty] | 2021-12-29 | 29 | 5.3237 | 0.99882 | 305.213 | 0.35921
[5 empty] | 2021-12-30 | 30 | 3.2579 | 0.98694 | 16.292 | 0.21562
[5 empty] | 2021-12-31 | 31 | 3.1918 | 0.98903 | 33.579 | 0.37255
Formulas:
Energy Export = Daily_Perf[timestamp]

## Figure daily wind_1
Intentionally blank

## 9. Supplemental
Milford Only
Month | Actual | Plan | Cumulative Actual | Cumulative Plan | Forecast | Guaranteed Quantity
July | 20741 | 18887 | 20741 | 18887 |  | 183900
August | 20777 | 19873 | 41518 | 38760 | 41518 | 183900
September |  | 15978 |  | 54738 | 57496 | 183900
October |  | 15063 |  | 69801 | 72559 | 183900
November |  | 13075 |  | 82876 | 85634 | 183900
December |  | 13288 |  | 96164 | 98922 | 183900
January |  | 13716 |  | 109880 | 112638 | 183900
February |  | 12893 |  | 122773 | 125531 | 183900
March |  | 16659 |  | 139432 | 142190 | 183900
April |  | 19305 |  | 158737 | 161495 | 183900
May |  | 18917 |  | 177654 | 180412 | 183900
June |  | 19445 |  | 197099 | 199857 | 183900
| Contract YTD Actual | Contract YTD Expected | Contract FY Forecast | FY Guaranteed Quantity
(MWh) | 41518 | 38760 | 0 | 183900
Note on F3: Sarie Lovell: Expecting a 1% increase in Clipper production availability due to turbines returned to service in March, which when combined with GE nameplate = 0.71% increase overall

## loss categories
lost energy by category -> lost production signal 3192 (downtime + curtailment) | [7 empty] | total curtailed volume in MWh--> | 0 | total -> | 0 | 0 | 0 | 0 | 0 | 0 | 5.0893 | 0 | 0 | 15.6663 | 0 | 0 | 43.7283 | 0 | 0 | 0 | 0 | 237.129 | 0 | 0 | 0 | 0 | 105.8062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | offline | turbine | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Economic Curtailment |  | Environmental | Environmental | Environmental | Environmental | Environmental | Environmental | Environmental | Environmental - Bird/Bat | Environmental - Icing | Excluded | Manufacturer - Blade Repair | Manufacturer - Blade Repair | Manufacturer - Fault | Manufacturer - Fault | Manufacturer - Gearbox | Manufacturer - Generator | Manufacturer - Other | Manufacturer - Planned Maintenance | Manufacturer - Planned Maintenance | Manufacturer - Planned Maintenance | Not Categorized | Not Categorized | Not Categorized | Not Categorized | Owner | Owner - Repair | Owner - Repair | Owner - Repair | Utility/BOP | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | project |  | project | project | project | project | project | project | project | project | contract | exclude | contract | contract | contract | contract | contract | contract | contract | contract | contract | project | project | project | project | project | project | project | project | project | project | 0 | 0 | 0 | 0 | 0 | 0
| 407.4191 | 280.8573 | 391.7528 | 15.6663 | 154.6238 |  |  |  | project |  | turbine | turbine | turbine | turbine | turbine | turbine | turbine | project | turbine | exclude | turbine | turbine | turbine | turbine | turbine | turbine | turbine | exclude | exclude | exclude | turbine | turbine | turbine | turbine | turbine | project | project | turbine | project | 0 | 0 | 0 | 0 | 0 | 0
turbine | total | contract | project | excluded | turbine | offline | curtailment |  | Calculated Curtailment Report |  | Environmental - ENV - High Temp | Environmental - ENV - High Wind Speed | Environmental - ENV - Lightning | Environmental - ENV - Low Temp | Environmental - ENV - Low Wind | Environmental - ENV - Other | Environmental - ENV - Out of Specification | Environmental - ENV - Bird/Bat | Environmental - ENV - Icing | Utility - CRT - Curtailment Pause Over RCS | Manufacturer - FTH - Repair - Blade | Manufacturer - FTH - Repair - Blade (Reimbursable) | Manufacturer - FTH - Fault | Manufacturer - FTH - Repair/Troubleshooting/Inspection | Manufacturer - FTH - Repair - Gearbox | Manufacturer - FTH - Repair - Generator | Manufacturer - TCH - Technical Standby Normal Test | Manufacturer - PTH - PM - Scheduled | Manufacturer - PTH - Planned Corrective Action | Manufacturer - PTH - PM (Contract Exempt) | Communication Offline | Manufacturer - PTH - Repair - Blade | Not Categorized | Owner - PTH - Planned Maintenance | Owner - FTH - Other | Owner - FTH - Repair - BOP | Owner - PTH - Planned Corrective Action (BOP) | Owner - FTH - Repair - Blade | Utility - CRT - Curtailment Offtaker | 0 | 0 | 0 | 0 | 0 | 0
Weaver 3 | 22.4453 | 15.4206 | 17.5807 | 4.8645 | 2.7985 | 15.4206 | 0 |  | 0 | WW-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024813 | 0 | 0 | 4.8645 | 0 | 0 | 0.63837 | 0 | 0 | 0 | 0 | 14.7822 | 0 | 0 | 0 | 0 | 2.1354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 4 | 5.64 | 1.2664 | 2.5891 | 3.0508 | 1.3228 | 1.2664 | 0 |  | 0 | WW-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44613 | 0 | 0 | 3.0508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2664 | 0 | 0 | 0 | 0 | 0.87666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 5 | 29.4397 | 27.3974 | 28.6613 | 0.77843 | 1.2663 | 27.3974 | 0 |  | 0 | WW-5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23225 | 0 | 0 | 0.77843 | 0 | 0 | 0.0024889 | 0 | 0 | 0 | 0 | 27.395 | 0 | 0 | 0 | 0 | 1.0316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 6 | 4.434 | 1.9486 | 3.5767 | 0.85733 | 1.712 | 1.9486 | 0 |  | 0 | WW-6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0496 | 0 | 0 | 0.85733 | 0 | 0 | 0.083968 | 0 | 0 | 0 | 0 | 1.8646 | 0 | 0 | 0 | 0 | 1.5784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 7 | 21.6533 | 20.1154 | 21.201 | 0.45231 | 2.248 | 20.1154 | 0 |  | 0 | WW-7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 0 | 0 | 0.45231 | 0 | 0 | 1.1624 | 0 | 0 | 0 | 0 | 18.953 | 0 | 0 | 0 | 0 | 0.85319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 8 | 31.0136 | 30.2694 | 30.8737 | 0.13985 | 1.8343 | 30.2694 | 0 |  | 0 | WW-8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0082167 | 0 | 0 | 0.13985 | 0 | 0 | 1.2299 | 0 | 0 | 0 | 0 | 29.0395 | 0 | 0 | 0 | 0 | 0.59614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 9 | 35.038 | 33.8591 | 34.9622 | 0.075817 | 1.1134 | 33.8591 | 0 |  | 0 | WW-9 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018281 | 0 | 0 | 0.075817 | 0 | 0 | 0.01025 | 0 | 0 | 0 | 0 | 33.8488 | 0 | 0 | 0 | 0 | 1.0849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 10 | 34.112 | 28.3307 | 33.5551 | 0.55688 | 27.9087 | 28.3307 | 0 |  | 0 | WW-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030917 | 0 | 0 | 0.55688 | 0 | 0 | 22.6843 | 0 | 0 | 0 | 0 | 5.6464 | 0 | 0 | 0 | 0 | 5.1935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 11 | 5.2632 | 3.2722 | 5.2632 | 0 | 2.1654 | 3.2722 | 0 |  | 0 | WW-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042567 | 0 | 0 | 0 | 0 | 0 | 0.17433 | 0 | 0 | 0 | 0 | 3.0978 | 0 | 0 | 0 | 0 | 1.9485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 12 | 4.948 | 3.9453 | 4.948 | 0 | 1.381 | 3.9453 | 0 |  | 0 | WW-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11473 | 0 | 0 | 0 | 0 | 0 | 0.3783 | 0 | 0 | 0 | 0 | 3.567 | 0 | 0 | 0 | 0 | 0.88798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 13 | 2.4142 | 1.0463 | 2.4142 | 0 | 1.5883 | 1.0463 | 0 |  | 0 | WW-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48792 | 0 | 0 | 0 | 0 | 0 | 0.22032 | 0 | 0 | 0 | 0 | 0.82595 | 0 | 0 | 0 | 0 | 0.88006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 14 | 25.5359 | 22.2231 | 25.5359 | 0 | 3.3128 | 22.2231 | 0 |  | 0 | WW-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.2231 | 0 | 0 | 0 | 0 | 2.9323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 15 | 11.8783 | 8.7348 | 10.0967 | 1.7816 | 1.3618 | 8.7348 | 0 |  | 0 | WW-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60529 | 0 | 0 | 1.7816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7348 | 0 | 0 | 0 | 0 | 0.75653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 16 | 24.0309 | 15.4118 | 23.5939 | 0.43696 | 9.1791 | 15.4118 | 0 |  | 0 | WW-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33115 | 0 | 0 | 0.43696 | 0 | 0 | 0.99697 | 0 | 0 | 0 | 0 | 14.4148 | 0 | 0 | 0 | 0 | 7.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 17 | 28.8717 | 25.4639 | 26.2 | 2.6717 | 15.264 | 25.4639 | 0 |  | 0 | WW-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23121 | 0 | 0 | 2.6717 | 0 | 0 | 14.528 | 0 | 0 | 0 | 0 | 10.9359 | 0 | 0 | 0 | 0 | 0.50483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 18 | 20.5159 | 20.1138 | 20.5159 | 0 | 0.40209 | 20.1138 | 0 |  | 0 | WW-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.1138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 19 | 14.7489 | 14.2353 | 14.7489 | 0 | 1.0357 | 14.2353 | 0 |  | 0 | WW-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020267 | 0 | 0 | 0 | 0 | 0 | 0.52216 | 0 | 0 | 0 | 0 | 13.7132 | 0 | 0 | 0 | 0 | 0.49326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 20 | 5.4736 | 1.5832 | 5.4736 | 0 | 4.6464 | 1.5832 | 0 |  | 0 | WW-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034497 | 0 | 0 | 0 | 0 | 0 | 0.75608 | 0 | 0 | 0 | 0 | 0.82717 | 0 | 0 | 0 | 0 | 3.8558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 22 | 71.5893 | 0.823 | 71.5893 | 0 | 70.7663 | 0.823 | 0 |  | 0 | WW-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.823 | 0 | 0 | 0 | 0 | 70.5838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 23 | 1.6848 | 0.8455 | 1.6848 | 0 | 0.83934 | 0.8455 | 0 |  | 0 | WW-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8455 | 0 | 0 | 0 | 0 | 0.57403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 24 | 4.6033 | 3.7145 | 4.6033 | 0 | 1.2198 | 3.7145 | 0 |  | 0 | WW-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36117 | 0 | 0 | 0 | 0 | 0 | 0.3309 | 0 | 0 | 0 | 0 | 3.3836 | 0 | 0 | 0 | 0 | 0.52769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weaver 25 | 2.0853 | 0.83711 | 2.0853 | 0 | 1.2577 | 0.83711 | 0 |  | 0 | WW-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58752 | 0 | 0 | 0 | 0 | 0 | 0.0095558 | 0 | 0 | 0 | 0 | 0.82755 | 0 | 0 | 0 | 0 | 0.66063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## YTD_Perf
month | Net Energy (MWh) | Budget Energy (MWh) | Capacity Factor (%) | Contract Availability (%) | Turbine Mechanical Availability (%) | Project Availability (%) | Budget Availability (%) | Performance Index (%) | Wind Speed (m/s) | Budget Wind Speed (m/s) | Total Turbine Hours | Contract Lost Energy (MWh) | Turbine Mechanical Lost Energy (MWh) | Project Lost Energy (MWh)
1 |  | 23466.517 |  |  |  |  | 0.965 |  |  | 8.1
2 |  | 21112.238 |  |  |  |  | 0.965 |  |  | 8.14
3 |  | 23626.863 |  |  |  |  | 0.965 |  |  | 8.3
4 |  | 19939.899 |  |  |  |  | 0.965 |  |  | 7.48
5 |  | 15744.38 |  |  |  |  | 0.965 |  |  | 6.65
6 |  | 13169.845 |  |  |  |  | 0.965 |  |  | 6.26
7 |  | 11649.166 |  |  |  |  | 0.965 |  |  | 5.89
8 |  | 10887.875 |  |  |  |  | 0.965 |  |  | 5.88
9 |  | 14415.958 |  |  |  |  | 0.965 |  |  | 6.58
10 |  | 20804.727 |  |  |  |  | 0.965 |  |  | 7.47
11 |  | 20941.379 |  |  |  |  | 0.965 |  |  | 7.64
12 | 24223.192 | 22899.871 | 0.4484580408187447 | 0.9889078334112458 | 0.9938626969454368 | 0.9845955982816258 | 0.965 | 0.9834158415577609 | 7.922528767901752 | 7.83 | 16368.0 | 280.857310797482 | 154.62380111715225 | 391.7528030565646

## Faults
Code | Fault | Count | Downtime (hrs) | Lost Energy (MWh) | Number of Turbines Impacted
900 | Pause pressed on keyboard | 59 | 150.9281 | 237.129 | 22
5179 | Fire cylinder gas level low | 2 | 260.4089 | 69.099 | 1
3719 | TowAcc Y,Extreme: m/s^ | 34 | 4.4142 | 18.4519 | 15
110 | Boat action curtailment | 222 | 264.8333 | 17.956 | 22
309 | Pause over RCS | 191 | 23.2544 | 15.9655 | 11
5101 | HiTempChokeWind:Mod; °C | 14 | 3.5236 | 14.1642 | 1
296 | Tow. acc. X,Alarm: m/s^ | 14 | 5.1444 | 14.1077 | 1
4518 | HubSafty HydrPres Low BldC | 3 | 2.2661 | 6.3339 | 3
3234 | PitchAccumulatorTestAccFailed | 2 | 1.4492 | 3.5616 | 1
356 | Extreme yawerror m/s° | 16 | 0.5225 | 2.6488 | 12
3273 | YawUntwistCCW: Code,° | 89 | 32.2503 | 2.4157 | 22
4517 | HubSafty HydrPres Low BldB | 3 | 0.54028 | 1.7875 | 3
6284 | EMC valves test active | 22 | 0.48944 | 1.3679 | 11
3798 | HubSafetySystem EncoderC,EC: | 9 | 0.26889 | 0.9816 | 1
4245 | ExtConverterStopArcDetected | 1 | 0.15667 | 0.52215 | 1
297 | Tow. acc. Y,Alarm: m/s^ | 2 | 0.043611 | 0.30691 | 1
6290 | Pitch accu. test active | 15 | 0.16389 | 0.25857 | 8
3129 | DODP Valve Failure | 2 | 0.13528 | 0.23357 | 1
176 | Error on all wind sensors | 3 | 0.32667 | 0.083968 | 1
3272 | YawUntwistCW: Code,-° | 6 | 1.81 | 0.02475 | 1
3562 | Overspeed Guard Error | 1 | 0.15972 | 0.0095558 | 1
3121 | PitchValBErr,VelocityBmm/s | 1 | 0.0022222 | 0.0061764 | 1
3009 | HydrOilTempHigh°C | 1 | 0.76111 | 0.0024889 | 1
343 | Encoder signal error : | 1 | 0.0325 | 0.00063333 | 1
2981 | MainBearLubrReservoirLevelLow | 5 | 2792.3608 | 0 | 4

## Turbine_Perf
Turbine | Energy Export (MWh) | Capacity Factor | Wind Speed (m/s) | Contract Lost Energy (MWh) | Turbine Lost Energy (MWh) | Project Lost Energy (MWh) | Performance Index
WW-3 | 1040.019 | 0.4235984848484849 | 7.451628115876937 | 15.420573575808577 | 2.798536704997789 | 17.58074040870149 | 0.9828506554212688
WW-4 | 1086.746 | 0.44263033561420667 | 7.8317018410417605 | 1.26635 | 1.3227904087014921 | 2.589140408701492 | 0.9907240399898978
WW-5 | 1055.195 | 0.429779651352232 | 7.5419855920756405 | 27.397447222222226 | 1.2662950173431948 | 28.66125330194359 | 0.9828541029204908
WW-6 | 1073.404 | 0.4371961550993809 | 7.96234318996416 | 1.9486096734892786 | 1.7120125612028438 | 3.576654179136567 | 0.9522172962529115
WW-7 | 1088.642 | 0.44340257412838063 | 7.784183329588858 | 20.115395762627546 | 2.2479770833333332 | 21.200999841617932 | 0.9733027758187478
WW-8 | 1181.301 | 0.48114247311827957 | 8.249438706780419 | 30.26938647623332 | 1.8342529487179484 | 30.873739424951268 | 0.9794374360192892
WW-9 | 1124.325 | 0.4579362170087977 | 7.949528301886791 | 33.85905974658869 | 1.1133917687160335 | 34.96220151530473 | 0.9785353739147293
WW-10 | 1065.674 | 0.4340477354187032 | 7.822985409652075 | 28.33071179546591 | 27.908716198301182 | 33.555082864967844 | 0.9696145493760746
WW-11 | 1140.884 | 0.4646806777451939 | 7.84883512544803 | 3.272152777777777 | 2.165413420523405 | 5.263232864967849 | 0.9715523993910754
WW-12 | 1156.208 | 0.4709221244705116 | 7.802598566308243 | 3.945316666666666 | 1.3810181544547642 | 4.94803482112143 | 0.9757093887664494
WW-13 | 1024.787 | 0.4173945096122516 | 7.480062724014338 | 1.0462688106899463 | 1.5882999999999998 | 2.41425 | 0.9786415079244506
WW-14 | 1089.485 | 0.44374592701205606 | 7.423023360287512 | 22.223085828460036 | 3.312812113390565 | 25.5358979418506 | 1.031153516653082
WW-15 | 1113.237 | 0.45342008797653965 | 7.801550213435181 | 8.734838333333336 | 1.361820258457859 | 10.096658591791195 | 0.9749164927817181
WW-16 | 1120.916 | 0.4565477354187032 | 7.778678948550885 | 15.411764999999999 | 9.179128696296296 | 23.593925362962963 | 0.9845324005797146
WW-17 | 1334.034 | 0.543350439882698 | 8.796811138558274 | 25.463916666666663 | 15.264041348374432 | 26.19996121701154 | 0.9800247457020603
WW-18 | 1348.888 | 0.5494004561746497 | 8.93266726537943 | 20.113758333333333 | 0.4020933333333333 | 20.515851666666666 | 0.9724163111014351
WW-19 | 1243.662 | 0.5065420332355817 | 8.334336402425334 | 14.235341628118686 | 1.0356833333333333 | 14.748867543859648 | 0.9711841199699512
WW-20 | 1108.965 | 0.4516801075268817 | 7.6634856630824375 | 1.58325 | 4.646412227204984 | 5.473578893871651 | 0.9739961194031143
WW-22 | 1049.749 | 0.4275615021179538 | 7.426769713261648 | 0.8229999999999997 | 70.76630428523232 | 71.58930428523232 | 1.1136446487211913
WW-23 | 1115.34 | 0.4542766373411535 | 7.756294802867383 | 0.8455 | 0.8393353276353275 | 1.6848353276353274 | 0.9718013135336233
WW-24 | 1178.872 | 0.4801531443466928 | 8.150134408602153 | 3.7144716666666664 | 1.2197579638009048 | 4.603329630467571 | 0.9552005678524818
WW-25 | 1299.139 | 0.5291377484522646 | 8.517540322580645 | 0.8371108333333331 | 1.257707963800905 | 2.0852629638009046 | 0.9708387521769815

## Category_Loss
Category | Lost Energy (MWh)
Environmental | 5.0893
Environmental - Icing | 0
Manufacturer - Fault | 149.5345
Manufacturer - Blade Repair | 0
Manufacturer - Gearbox | 0
Manufacturer - Generator | 0
Manufacturer - Planned Maintenance | 237.129
Manufacturer - Other | 0
Not Categorized | 0
Owner | 0
Owner - Repair | 0
Utility/BOP | 0
Environmental - Bird/Bat | 0

## Loss_by_Turbine
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10 | Column11 | Column12 | Column13 | Column14 | Column15 | Column16 | Column17 | Column18 | Column19 | Column20 | Column21 | Column22 | Column23 | Column24 | Column25 | Column26 | Column27 | Column28 | Column29 | Column30 | Column31 | Column32
turbine | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline | offline
| Environmental | Environmental | Environmental | Environmental | Environmental | Environmental | Environmental | Environmental - Bird/Bat | Environmental - Icing | Excluded | Manufacturer - Blade Repair | Manufacturer - Blade Repair | Manufacturer - Fault | Manufacturer - Fault | Manufacturer - Gearbox | Manufacturer - Generator | Manufacturer - Other | Manufacturer - Planned Maintenance | Manufacturer - Planned Maintenance | Manufacturer - Planned Maintenance | Not Categorized | Not Categorized | Not Categorized | Not Categorized | Owner | Owner - Repair | Owner - Repair | Owner - Repair | Utility/BOP | Utility/BOP | Utility/BOP
| project | project | project | project | project | project | project | project | contract | exclude | contract | contract | contract | contract | contract | contract | contract | contract | contract | project | project | project | project | project | project | project | project | project | project | project | project
| turbine | turbine | turbine | turbine | turbine | turbine | turbine | project | turbine | exclude | turbine | turbine | turbine | turbine | turbine | turbine | turbine | exclude | exclude | exclude | turbine | turbine | turbine | turbine | turbine | project | project | turbine | project | project | project
| Environmental - ENV - High Temp | Environmental - ENV - High Wind Speed | Environmental - ENV - Lightning | Environmental - ENV - Low Temp | Environmental - ENV - Low Wind | Environmental - ENV - Other | Environmental - ENV - Out of Specification | Environmental - ENV - Bird/Bat | Environmental - ENV - Icing | Utility - CRT - Curtailment Pause Over RCS | Manufacturer - FTH - Repair - Blade | Manufacturer - FTH - Repair - Blade (Reimbursable) | Manufacturer - FTH - Fault | Manufacturer - FTH - Repair/Troubleshooting/Inspection | Manufacturer - FTH - Repair - Gearbox | Manufacturer - FTH - Repair - Generator | Manufacturer - TCH - Technical Standby Normal Test | Manufacturer - PTH - PM - Scheduled | Manufacturer - PTH - Planned Corrective Action | Manufacturer - PTH - PM (Contract Exempt) | Communication Offline | Manufacturer - PTH - Repair - Blade | Not Categorized | Owner - PTH - Planned Maintenance | Owner - FTH - Other | Owner - FTH - Repair - BOP | Owner - PTH - Planned Corrective Action (BOP) | Owner - FTH - Repair - Blade | Utility - CRT - Curtailment Offtaker | Utility - CRT - Curtailment Other | Utility - FTH - BOP out of Specification
WW-3 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.024812828947368422 | 0.0 | 0.0 | 4.864513589897947 | 0.0 | 0.0 | 0.6383698721048734 | 0.0 | 0.0 | 0.0 | 0.0 | 14.782203703703704 | 0.0 | 0.0 | 0.0 | 0.0 | 2.135354003945547 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-4 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.4461331993177387 | 0.0 | 0.0 | 3.0508358121201695 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 1.26635 | 0.0 | 0.0 | 0.0 | 0.0 | 0.8766572093837535 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-5 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.2322523624011008 | 0.0 | 0.0 | 0.778433779956427 | 0.0 | 0.0 | 0.0024889376218323587 | 0.0 | 0.0 | 0.0 | 0.0 | 27.394958284600392 | 0.0 | 0.0 | 0.0 | 0.0 | 1.0315537173202616 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-6 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.049600000000000005 | 0.0 | 0.0 | 0.8573322549019606 | 0.0 | 0.0 | 0.08396805555555555 | 0.0 | 0.0 | 0.0 | 0.0 | 1.864641617933723 | 0.0 | 0.0 | 0.0 | 0.0 | 1.5784445056472882 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-7 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.2324166666666666 | 0.0 | 0.0 | 0.4523104861111111 | 0.0 | 0.0 | 1.1623730043429472 | 0.0 | 0.0 | 0.0 | 0.0 | 18.9530227582846 | 0.0 | 0.0 | 0.0 | 0.0 | 0.8531874123237192 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-8 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.008216666666666667 | 0.0 | 0.0 | 0.13984694444444445 | 0.0 | 0.0 | 1.2298999999999998 | 0.0 | 0.0 | 0.0 | 0.0 | 29.039486476233318 | 0.0 | 0.0 | 0.0 | 0.0 | 0.596136282051282 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-9 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.018281100217864926 | 0.0 | 0.0 | 0.07581666666666667 | 0.0 | 0.0 | 0.010249999999999993 | 0.0 | 0.0 | 0.0 | 0.0 | 33.84880974658869 | 0.0 | 0.0 | 0.0 | 0.0 | 1.0848606684981685 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-10 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.030916666666666662 | 0.0 | 0.0 | 0.5568833333333333 | 0.0 | 0.0 | 22.684345128799244 | 0.0 | 0.0 | 0.0 | 0.0 | 5.646366666666666 | 0.0 | 0.0 | 0.0 | 0.0 | 5.193454402835271 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-11 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.04256666666666666 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.17433333333333334 | 0.0 | 0.0 | 0.0 | 0.0 | 3.097819444444444 | 0.0 | 0.0 | 0.0 | 0.0 | 1.948513420523405 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-12 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.11473482112143102 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.37829999999999997 | 0.0 | 0.0 | 0.0 | 0.0 | 3.567016666666666 | 0.0 | 0.0 | 0.0 | 0.0 | 0.8879833333333331 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-13 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.4879166666666666 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.2203188106899463 | 0.0 | 0.0 | 0.0 | 0.0 | 0.8259499999999999 | 0.0 | 0.0 | 0.0 | 0.0 | 0.880064522643387 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-14 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.3804634952766531 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 22.223085828460036 | 0.0 | 0.0 | 0.0 | 0.0 | 2.932348618113912 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-15 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.6052929471743711 | 0.0 | 0.0 | 1.7816149999999997 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 8.734838333333336 | 0.0 | 0.0 | 0.0 | 0.0 | 0.7565273112834877 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-16 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.3311533333333333 | 0.0 | 0.0 | 0.43696463703703703 | 0.0 | 0.0 | 0.9969683333333331 | 0.0 | 0.0 | 0.0 | 0.0 | 14.414796666666666 | 0.0 | 0.0 | 0.0 | 0.0 | 7.851007029629629 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-17 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.23121121701154607 | 0.0 | 0.0 | 2.6717333333333335 | 0.0 | 0.0 | 14.527996798029552 | 0.0 | 0.0 | 0.0 | 0.0 | 10.935919868637109 | 0.0 | 0.0 | 0.0 | 0.0 | 0.5048333333333334 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-18 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.4020933333333333 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 20.113758333333333 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-19 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.020266666666666665 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.5221574175923712 | 0.0 | 0.0 | 0.0 | 0.0 | 13.713184210526315 | 0.0 | 0.0 | 0.0 | 0.0 | 0.4932592490742954 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-20 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.03449705882352941 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.7560833333333333 | 0.0 | 0.0 | 0.0 | 0.0 | 0.8271666666666666 | 0.0 | 0.0 | 0.0 | 0.0 | 3.8558318350481215 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-22 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.1824871794871795 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.8229999999999997 | 0.0 | 0.0 | 0.0 | 0.0 | 70.58381710574514 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-23 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.26530199430199425 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.8455 | 0.0 | 0.0 | 0.0 | 0.0 | 0.5740333333333333 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-24 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.3611705128205127 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.33089999999999997 | 0.0 | 0.0 | 0.0 | 0.0 | 3.3835716666666666 | 0.0 | 0.0 | 0.0 | 0.0 | 0.5276874509803922 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
WW-25 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.5875187971342383 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.009555833333333333 | 0.0 | 0.0 | 0.0 | 0.0 | 0.8275549999999998 | 0.0 | 0.0 | 0.0 | 0.0 | 0.6606333333333334 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0

## Daily_Perf
timestamp | day | Wind speed | Energy Export | Project availability | Project Lost Energy (MWh) | Wind speed (met mast)
2021-12-01 | 1 | 5.2113 | 309.506 | 0.96991 | 9.6015
2021-12-02 | 2 | 9.0669 | 1166.517 | 0.96607 | 40.9699
2021-12-03 | 3 | 12.7018 | 1552.859 | 0.99575 | 6.6274
2021-12-04 | 4 | 5.7317 | 445.284 | 0.99976 | 0.10694
2021-12-05 | 5 | 6.8902 | 656.298 | 0.99971 | 0.18853
2021-12-06 | 6 | 13.3929 | 1497.628 | 0.95642 | 68.2349
2021-12-07 | 7 | 9.5433 | 1132.691 | 0.97673 | 26.9876
2021-12-08 | 8 | 6.3117 | 514.088 | 0.99332 | 3.4595
2021-12-09 | 9 | 6.6451 | 535.453 | 0.99093 | 4.8992
2021-12-10 | 10 | 5.3271 | 295.377 | 0.97144 | 8.6845
2021-12-11 | 11 | 9.9533 | 1146.712 | 0.99986 | 0.16575
2021-12-12 | 12 | 12.8009 | 1627 | 0.99967 | 0.53228
2021-12-13 | 13 | 9.5901 | 1217.759 | 0.98432 | 19.3956
2021-12-14 | 14 | 10.4844 | 1345.228 | 0.97416 | 35.6869
2021-12-15 | 15 | 5.7092 | 470.775 | 0.99869 | 0.61754
2021-12-16 | 16 | 7.373 | 782.197 | 0.99844 | 1.2232
2021-12-17 | 17 | 11.3716 | 1519.733 | 0.98684 | 20.2631
2021-12-18 | 18 | 6.0012 | 494.609 | 0.99875 | 0.61671
2021-12-19 | 19 | 7.3796 | 688.499 | 0.99937 | 0.43587
2021-12-20 | 20 | 6.4104 | 584.332 | 0.99696 | 1.78
2021-12-21 | 21 | 7.6063 | 823.826 | 0.9996 | 0.3309
2021-12-22 | 22 | 11.0204 | 1152.665 | 0.98651 | 15.7621
2021-12-23 | 23 | 12.3216 | 1356.347 | 0.9776 | 31.0786
2021-12-24 | 24 | 9.2461 | 1167.14 | 0.99985 | 0.17953
2021-12-25 | 25 | 5.6392 | 407.107 | 0.99704 | 1.2096
2021-12-26 | 26 | 6.588 | 568.375 | 0.95242 | 28.3973
2021-12-27 | 27 | 7.1341 | 700.215 | 0.95575 | 32.416
2021-12-28 | 28 | 6.3736 | 526.168 | 0.94444 | 30.9544
2021-12-29 | 29 | 5.3237 | 305.213 | 0.99882 | 0.35921
2021-12-30 | 30 | 3.2579 | 16.292 | 0.98694 | 0.21562
2021-12-31 | 31 | 3.1918 | 33.579 | 0.98903 | 0.37255